## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | PRoject1
Created By | : | pendy
Customer Input
Selected Model / Type | : | UAM100C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 25.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 0.00 |  | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 8.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (MS Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 100.0 |  |  |  |  | 100.0 |  |  |  |  | TR
|  |  | 351.7 |  |  |  |  | 351.7 |  |  |  |  | kW
Current | : | Compressor | 201 |  |  |  |  | 174 |  |  |  |  | A
|  | Fan | 24 |  |  |  |  | 24 |  |  |  |  | A
|  | Total | 225 |  |  |  |  | 198 |  |  |  |  | A
Power Input | : | Compressor | 116.4 |  |  |  |  | 94.52 |  |  |  |  | kW
|  | Fan | 16.00 |  |  |  |  | 16.00 |  |  |  |  | kW
|  | Total | 132.4 |  |  |  |  | 110.5 |  |  |  |  | kW
COP | : |  | 2.656 |  |  |  |  | 3.182 |  |  |  |  | kW/kW
Flow Rate | : |  | 54.56 |  |  |  |  | 50.00 |  |  |  |  | m³/h
Pressure Drop | : |  | 53.6 |  |  |  |  | 46.8 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the MS2449 standard condition of EWT/LWT of 12.22/6.67?C, and ambient temperature of 35.0?C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m?.K/kW, and rating altitute at 0 m.
Part Load Performance
MPLV | : |  | 3.198 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Corresponding Capacity | : |  | 100.0 | 96.0 | 87.8 | 69.5 | 61.3 | 53.1 | 34.7 | 26.6 | - | - | %
Total Cooling Capacity | : |  | 100.0 | 96.04 | 87.85 | 69.49 | 61.30 | 53.10 | 34.75 | 26.55 | - | - | TR
Total Cooling Capacity | : |  | 351.7 | 337.8 | 309.0 | 244.4 | 215.6 | 186.8 | 122.2 | 93.38 | - | - | kW
Total Power Input | : |  | 110.5 | 85.45 | 80.33 | 60.38 | 55.26 | 50.14 | 30.19 | 25.07 | - | - | kW
Total Current | : |  | 198 | 153 | 144 | 108 | 99 | 91 | 54 | 46 | - | - | A
COP | : |  | 3.182 | 3.953 | 3.846 | 4.048 | 3.901 | 3.725 | 4.048 | 3.725 | - | - | kW/kW
Ambient Temperature | : |  | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | - | - | °C
EEWT | : |  | 14.06 | 13.82 | 13.32 | 12.21 | 11.71 | 11.22 | 10.10 | 9.61 | - | - | °C
ELWT | : |  | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | - | - | °C
Flow Rate | : |  | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | - | - | m³/h
Pressure Drop | : |  | 46.8 | 46.8 | 46.8 | 46.8 | 46.8 | 46.8 | 46.8 | 46.8 | - | - | kPa
Others
MCA | : |  | 3.198 1: 282 | A
No. of Refrigerant Circuit | : |  | 3.198 1: 2 | -
Refrigerant Type : | : |  | 3.198 1: R410A | -
Refrigerant Charge : | : | System 1/2 | 3.198 1: 35.0 / 35.0 | kg/System
Chiller Dimension | : | W / D / H | 3.198 1: 2237 / 4163 / 2156 | mm
Weight | : | Shipping | 3.198 1: 3048 | kg
|  | Operating | 3.198 1: 3239 | kg
Evaporator
Type | : |  | 3.198 1: S&T | -
Inlet/Outlet Diameter | : |  | 3.198 1: 5" Victaulic Joint
Flow Rate | : | Min / Max | 3.198 1: 16.40 / 70.40 | m³/h
Pressure Drop | : | Min / Max | 3.198 1: 7.00 / 79.0 | kPa
Compressor
Quantity | : | System 1/2 | 3.198 1: 2 / 2
Type | : |  | 3.198 1: Hermetic-sealed (Scroll) | -
Oil Charge | : | System 1/2 | 3.198 1: 13.4 / 13.4 | L/System
Condenser
Coil
Tube | : | Type | 3.198 1: Copper | -
Fin | : | Type | 3.198 1: Aluminium | -
Surface Area/ Coil | : |  | 3.198 1: 15.36 | m²/Coil
Fan
Type/ Drive | : |  | 3.198 1: Axial / Direct | -
Quantity per System | : |  | 3.198 1: 4 | -
Certified in accordance with the AHRI Air-Cooled Water-Chilling Packages Certification Program, which is based on AHRI Standard 550/590 (I-P) and AHRI Standard 551/591 (SI). Certified Units may be found in the AHRI Directory at www.ahridirectory.org
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 |  |  | 3.198 8: 08-Dec, 2022 12:22 | Page : 1/2