## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | TESt
Created By | : | Kelvin
Customer Input
Selected Model / Type | : | UAMH50A3F |  |  | / | Inverter Speed (Hybrid) Scroll Chiller Version A
Ambient Temperature | : |  | 25.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 0.00 |  | °C |  |  | Voltage |  | : | 400 |  | V
|  | LWT | 8.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (MS Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 50.15 |  |  |  |  | 50.00 |  |  |  |  | TR
|  |  | 176.4 |  |  |  |  | 175.9 |  |  |  |  | kW
Current | : | Compressor | 93 |  |  |  |  | 61 |  |  |  |  | A
|  | Fan | 9 |  |  |  |  | 8 |  |  |  |  | A
|  | Total | 102 |  |  |  |  | 69 |  |  |  |  | A
Power Input | : | Compressor | 55.02 |  |  |  |  | 33.60 |  |  |  |  | kW
|  | Fan | 5.400 |  |  |  |  | 4.500 |  |  |  |  | kW
|  | Total | 60.42 |  |  |  |  | 38.10 |  |  |  |  | kW
COP | : |  | 2.919 |  |  |  |  | 4.616 |  |  |  |  | kW/kW
Flow Rate | : |  | 27.36 |  |  |  |  | 50.00 |  |  |  |  | m³/h
Pressure Drop | : |  | 15.4 |  |  |  |  | 39.2 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the MS2449 standard condition of EWT/LWT of 12.22/6.67?C, and ambient temperature of 35.0?C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m?.K/kW, and rating altitute at 0 m.
Part Load Performance
MPLV | : |  | 3.686 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Corresponding Capacity | : |  | 100.0 | 90.0 | 80.0 | 70.0 | 60.0 | 50.0 | 40.0 | 30.0 | 20.0 | 10.0 | %
Total Cooling Capacity | : |  | 50.00 | 45.00 | 40.00 | 35.00 | 30.00 | 25.00 | 20.00 | 15.00 | 10.00 | 5.000 | TR
Total Cooling Capacity | : |  | 175.9 | 158.3 | 140.7 | 123.1 | 105.5 | 87.93 | 70.34 | 52.76 | 35.17 | 17.59 | kW
Total Power Input | : |  | 38.10 | 34.09 | 31.61 | 27.58 | 22.89 | 19.09 | 17.30 | 13.48 | 8.626 | 5.027 | kW
Total Current | : |  | 69 | 63 | 56 | 50 | 41 | 36 | 30 | 24 | 15 | 10 | A
COP | : |  | 4.616 | 4.642 | 4.450 | 4.462 | 4.610 | 4.606 | 4.066 | 3.914 | 4.077 | 3.498 | kW/kW
Ambient Temperature | : |  | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | °C
EEWT | : |  | 11.03 | 10.73 | 10.42 | 10.12 | 9.82 | 9.51 | 9.21 | 8.91 | 8.61 | 8.30 | °C
ELWT | : |  | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | °C
Flow Rate | : |  | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | m³/h
Pressure Drop | : |  | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | kPa
Others
MCA | : |  | 3.686 1: 133 | A
No. of Refrigerant Circuit | : |  | 3.686 1: 2 | -
Refrigerant Type : | : |  | 3.686 1: R410A | -
Refrigerant Charge : | : | System 1/2 | 3.686 1: 25.0 / 25.0 | kg/System
Chiller Dimension | : | W / D / H | 3.686 1: 2237 / 3263 / 2156 | mm
Weight | : | Shipping | 3.686 1: 2052 | kg
|  | Operating | 3.686 1: 2174 | kg
Evaporator
Type | : |  | 3.686 1: S&T | -
Inlet/Outlet Diameter | : |  | 3.686 1: 4" Victaulic Joint
Flow Rate | : | Min / Max | 3.686 1: 15.00 / 56.70 | m³/h
Pressure Drop | : | Min / Max | 3.686 1: 5.00 / 47.0 | kPa
Compressor
Quantity | : | System 1/2 | 3.686 1: 2 / 2
Type | : |  | 3.686 1: Hermetic-sealed (Scroll) | -
Oil Charge | : | System 1/2 | 3.686 1: 13.4 / 13.4 | L/System
Condenser
Coil
Tube | : | Type | 3.686 1: Copper | -
Fin | : | Type | 3.686 1: Aluminium | -
Surface Area/ Coil | : |  | 3.686 1: 11.52 | m²/Coil
Fan
Type/ Drive | : |  | 3.686 1: Axial / Direct | -
Quantity per System | : |  | 3.686 1: 3 | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 |  |  | 3.686 8: 08-Dec, 2022 17:28 | Page : 1/2