## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | Project Name CST
Created By | : | Cheong ST
Customer Input
Selected Model / Type | : | UAM60C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 35.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 11.00 |  | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 6.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 59.27 |  |  |  |  | 57.18 |  |  |  |  | TR
|  |  | 208.4 |  |  |  |  | 201.1 |  |  |  |  | kW
Current | : | Compressor | 115 |  |  |  |  | 115 |  |  |  |  | A
|  | Fan | 18 |  |  |  |  | 18 |  |  |  |  | A
|  | Total | 133 |  |  |  |  | 133 |  |  |  |  | A
Power Input | : | Compressor | 67.18 |  |  |  |  | 67.15 |  |  |  |  | kW
|  | Fan | 12.00 |  |  |  |  | 12.00 |  |  |  |  | kW
|  | Total | 79.18 |  |  |  |  | 79.15 |  |  |  |  | kW
COP | : |  | 2.632 |  |  |  |  | 2.541 |  |  |  |  | kW/kW
Flow Rate | : |  | 35.90 |  |  |  |  | 34.63 |  |  |  |  | m³/h
Pressure Drop | : |  | 37.9 |  |  |  |  | 35.8 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00?C, and ambient temperature of 35.0?C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m?.K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.750 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Corresponding Capacity | : |  | 100.0 | 75.0 | 50.0 | 25.0 | - | - | - | - | - | - | %
Total Cooling Capacity | : |  | 57.18 | 42.89 | 28.59 | 14.30 | - | - | - | - | - | - | TR
Total Cooling Capacity | : |  | 201.1 | 150.8 | 100.6 | 50.28 | - | - | - | - | - | - | kW
Total Power Input | : |  | 79.15 | 60.36 | 39.57 | 20.79 | - | - | - | - | - | - | kW
Total Current | : |  | 133 | 101 | 67 | 35 | - | - | - | - | - | - | A
COP | : |  | 2.541 | 2.499 | 2.541 | 2.419 | - | - | - | - | - | - | kW/kW
Ambient Temperature | : |  | 35.0 | 35.0 | 35.0 | 35.0 | - | - | - | - | - | - | °C
EEWT | : |  | 11.00 | 9.75 | 8.50 | 7.25 | - | - | - | - | - | - | °C
ELWT | : |  | 6.00 | 6.00 | 6.00 | 6.00 | - | - | - | - | - | - | °C
Flow Rate | : |  | 34.63 | 34.63 | 34.63 | 34.63 | - | - | - | - | - | - | m³/h
Pressure Drop | : |  | 35.8 | 35.8 | 35.8 | 35.8 | - | - | - | - | - | - | kPa
Others
MCA | : |  | 3.750 1: 164 | A
No. of Refrigerant Circuit | : |  | 3.750 1: 2 | -
Refrigerant Type : | : |  | 3.750 1: R410A | -
Refrigerant Charge : | : | System 1/2 | 3.750 1: 21.0 / 21.0 | kg/System
Chiller Dimension | : | W / D / H | 3.750 1: 2237 / 3263 / 2156 | mm
Weight | : | Shipping | 3.750 1: 2052 | kg
|  | Operating | 3.750 1: 2174 | kg
Evaporator
Type | : |  | 3.750 1: S&T | -
Inlet/Outlet Diameter | : |  | 3.750 1: 4" Victaulic Joint
Flow Rate | : | Min / Max | 3.750 1: 13.70 / 61.20 | m³/h
Pressure Drop | : | Min / Max | 3.750 1: 7.00 / 90.0 | kPa
Compressor
Quantity | : | System 1/2 | 3.750 1: 2 / 2
Type | : |  | 3.750 1: Hermetic-sealed (Scroll) | -
Oil Charge | : | System 1/2 | 3.750 1: 13.4 / 13.4 | L/System
Condenser
Coil
Tube | : | Type | 3.750 1: Copper | -
Fin | : | Type | 3.750 1: Aluminium | -
Surface Area/ Coil | : |  | 3.750 1: 11.52 | m²/Coil
Fan
Type/ Drive | : |  | 3.750 1: Axial / Direct | -
Quantity per System | : |  | 3.750 1: 3 | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 |  |  | 3.750 8: 09-Dec, 2022 08:10 | Page : 1/2