## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | :
Created By | :
Customer Input
Selected Model / Type | : | UAM80C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 25.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 11.00 |  | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 8.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 80.00 |  |  |  |  | 80.00 |  |  |  |  | TR
|  |  | 281.4 |  |  |  |  | 281.4 |  |  |  |  | kW
Current | : | Compressor | 161 |  |  |  |  | 140 |  |  |  |  | A
|  | Fan | 18 |  |  |  |  | 18 |  |  |  |  | A
|  | Total | 179 |  |  |  |  | 158 |  |  |  |  | A
Power Input | : | Compressor | 92.20 |  |  |  |  | 75.46 |  |  |  |  | kW
|  | Fan | 12.00 |  |  |  |  | 12.00 |  |  |  |  | kW
|  | Total | 104.2 |  |  |  |  | 87.46 |  |  |  |  | kW
COP | : |  | 2.700 |  |  |  |  | 3.217 |  |  |  |  | kW/kW
Flow Rate | : |  | 48.45 |  |  |  |  | 53.87 |  |  |  |  | m³/h
Pressure Drop | : |  | 37.4 |  |  |  |  | 43.8 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00?C, and ambient temperature of 35.0?C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m?.K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.926 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Corresponding Capacity | : |  | 100.0 | 93.3 | 87.1 | 66.4 | 60.1 | 53.9 | 33.2 | 27.0 | - | - | %
Total Cooling Capacity | : |  | 80.00 | 74.66 | 69.67 | 53.10 | 48.11 | 43.12 | 26.55 | 21.56 | - | - | TR
Total Cooling Capacity | : |  | 281.4 | 262.6 | 245.0 | 186.8 | 169.2 | 151.7 | 93.38 | 75.83 | - | - | kW
Total Power Input | : |  | 87.46 | 68.80 | 64.39 | 50.14 | 43.73 | 41.32 | 25.07 | 20.66 | - | - | kW
Total Current | : |  | 158 | 124 | 116 | 91 | 79 | 74 | 46 | 37 | - | - | A
COP | : |  | 3.217 | 3.817 | 3.806 | 3.725 | 3.869 | 3.670 | 3.725 | 3.670 | - | - | kW/kW
Ambient Temperature | : |  | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | - | - | °C
EEWT | : |  | 12.50 | 12.20 | 11.92 | 10.99 | 10.70 | 10.42 | 9.49 | 9.21 | - | - | °C
ELWT | : |  | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | - | - | °C
Flow Rate | : |  | 53.87 | 53.87 | 53.87 | 53.87 | 53.87 | 53.87 | 53.87 | 53.87 | - | - | m³/h
Pressure Drop | : |  | 43.8 | 43.8 | 43.8 | 43.8 | 43.8 | 43.8 | 43.8 | 43.8 | - | - | kPa
Others
MCA | : |  | 3.926 1: 223 | A
No. of Refrigerant Circuit | : |  | 3.926 1: 2 | -
Refrigerant Type : | : |  | 3.926 1: R410A | -
Refrigerant Charge : | : | System 1/2 | 3.926 1: 25.0 / 25.0 | kg/System
Chiller Dimension | : | W / D / H | 3.926 1: 2237 / 3263 / 2156 | mm
Weight | : | Shipping | 3.926 1: 2917 | kg
|  | Operating | 3.926 1: 3039 | kg
Evaporator
Type | : |  | 3.926 1: S&T | -
Inlet/Outlet Diameter | : |  | 3.926 1: 5" Victaulic Joint
Flow Rate | : | Min / Max | 3.926 1: 15.00 / 56.70 | m³/h
Pressure Drop | : | Min / Max | 3.926 1: 5.00 / 47.0 | kPa
Compressor
Quantity | : | System 1/2 | 3.926 1: 2 / 2
Type | : |  | 3.926 1: Hermetic-sealed (Scroll) | -
Oil Charge | : | System 1/2 | 3.926 1: 13.4 / 13.4 | L/System
Condenser
Coil
Tube | : | Type | 3.926 1: Copper | -
Fin | : | Type | 3.926 1: Aluminium | -
Surface Area/ Coil | : |  | 3.926 1: 11.52 | m²/Coil
Fan
Type/ Drive | : |  | 3.926 1: Axial / Direct | -
Quantity per System | : |  | 3.926 1: 3 | -
Certified in accordance with the AHRI Air-Cooled Water-Chilling Packages Certification Program, which is based on AHRI Standard 550/590 (I-P) and AHRI Standard 551/591 (SI). Certified Units may be found in the AHRI Directory at www.ahridirectory.org
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 |  |  | 3.926 8: 09-Dec, 2022 11:59 | Page : 1/2