## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | CSS Dec 09
Created By | : | lee ming yang
Customer Input
Selected Model / Type | : | UAM80C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 33.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 11.00 |  | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 6.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 80.00 |  |  |  |  | 80.00 |  |  |  |  | TR
|  |  | 281.4 |  |  |  |  | 281.4 |  |  |  |  | kW
Current | : | Compressor | 161 |  |  |  |  | 156 |  |  |  |  | A
|  | Fan | 18 |  |  |  |  | 18 |  |  |  |  | A
|  | Total | 179 |  |  |  |  | 174 |  |  |  |  | A
Power Input | : | Compressor | 92.20 |  |  |  |  | 88.51 |  |  |  |  | kW
|  | Fan | 12.00 |  |  |  |  | 12.00 |  |  |  |  | kW
|  | Total | 104.2 |  |  |  |  | 100.5 |  |  |  |  | kW
COP | : |  | 2.700 |  |  |  |  | 2.799 |  |  |  |  | kW/kW
Flow Rate | : |  | 48.45 |  |  |  |  | 48.45 |  |  |  |  | m³/h
Pressure Drop | : |  | 37.4 |  |  |  |  | 37.4 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00?C, and ambient temperature of 35.0?C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m?.K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.926 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Corresponding Capacity | : |  | 100.0 | 78.1 | 72.9 | 55.6 | 50.3 | 45.1 | 27.8 | 22.5 | - | - | %
Total Cooling Capacity | : |  | 80.00 | 62.50 | 58.30 | 44.47 | 40.27 | 36.07 | 22.23 | 18.03 | - | - | TR
Total Cooling Capacity | : |  | 281.4 | 219.8 | 205.0 | 156.4 | 141.6 | 126.8 | 78.19 | 63.42 | - | - | kW
Total Power Input | : |  | 100.5 | 78.90 | 73.86 | 57.29 | 50.25 | 47.22 | 28.65 | 23.61 | - | - | kW
Total Current | : |  | 174 | 137 | 128 | 100 | 87 | 81 | 50 | 41 | - | - | A
COP | : |  | 2.799 | 2.786 | 2.776 | 2.730 | 2.818 | 2.686 | 2.730 | 2.686 | - | - | kW/kW
Ambient Temperature | : |  | 33.0 | 33.0 | 33.0 | 33.0 | 33.0 | 33.0 | 33.0 | 33.0 | - | - | °C
EEWT | : |  | 11.00 | 9.91 | 9.64 | 8.78 | 8.52 | 8.25 | 7.39 | 7.13 | - | - | °C
ELWT | : |  | 6.00 | 6.00 | 6.00 | 6.00 | 6.00 | 6.00 | 6.00 | 6.00 | - | - | °C
Flow Rate | : |  | 48.45 | 48.45 | 48.45 | 48.45 | 48.45 | 48.45 | 48.45 | 48.45 | - | - | m³/h
Pressure Drop | : |  | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | - | - | kPa
Others
MCA | : |  | 3.926 1: 223 | A
No. of Refrigerant Circuit | : |  | 3.926 1: 2 | -
Refrigerant Type : | : |  | 3.926 1: R410A | -
Refrigerant Charge : | : | System 1/2 | 3.926 1: 25.0 / 25.0 | kg/System
Chiller Dimension | : | W / D / H | 3.926 1: 2237 / 3263 / 2156 | mm
Weight | : | Shipping | 3.926 1: 2917 | kg
|  | Operating | 3.926 1: 3039 | kg
Evaporator
Type | : |  | 3.926 1: S&T | -
Inlet/Outlet Diameter | : |  | 3.926 1: 5" Victaulic Joint
Flow Rate | : | Min / Max | 3.926 1: 15.00 / 56.70 | m³/h
Pressure Drop | : | Min / Max | 3.926 1: 5.00 / 47.0 | kPa
Compressor
Quantity | : | System 1/2 | 3.926 1: 2 / 2
Type | : |  | 3.926 1: Hermetic-sealed (Scroll) | -
Oil Charge | : | System 1/2 | 3.926 1: 13.4 / 13.4 | L/System
Condenser
Coil
Tube | : | Type | 3.926 1: Copper | -
Fin | : | Type | 3.926 1: Aluminium | -
Surface Area/ Coil | : |  | 3.926 1: 11.52 | m²/Coil
Fan
Type/ Drive | : |  | 3.926 1: Axial / Direct | -
Quantity per System | : |  | 3.926 1: 3 | -
Certified in accordance with the AHRI Air-Cooled Water-Chilling Packages Certification Program, which is based on AHRI Standard 550/590 (I-P) and AHRI Standard 551/591 (SI). Certified Units may be found in the AHRI Directory at www.ahridirectory.org
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 |  |  | 3.926 8: 14-Dec, 2022 13:51 | Page : 1/2