## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | hop
Created By | : | lee ming yang
Customer Input
Selected Model / Type | : | UAM40C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 33.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 11.00 |  | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 6.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 40.00 |  |  |  |  | 40.00 |  |  |  |  | TR
|  |  | 140.7 |  |  |  |  | 140.7 |  |  |  |  | kW
Current | : | Compressor | 81 |  |  |  |  | 78 |  |  |  |  | A
|  | Fan | 9 |  |  |  |  | 9 |  |  |  |  | A
|  | Total | 90 |  |  |  |  | 87 |  |  |  |  | A
Power Input | : | Compressor | 46.10 |  |  |  |  | 44.25 |  |  |  |  | kW
|  | Fan | 6.000 |  |  |  |  | 6.000 |  |  |  |  | kW
|  | Total | 52.10 |  |  |  |  | 50.25 |  |  |  |  | kW
COP | : |  | 2.700 |  |  |  |  | 2.799 |  |  |  |  | kW/kW
Flow Rate | : |  | 24.23 |  |  |  |  | 24.23 |  |  |  |  | m³/h
Pressure Drop | : |  | 51.2 |  |  |  |  | 51.2 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00?C, and ambient temperature of 35.0?C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m?.K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.739 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 2 | 3 | 4 | - | - | - | - | -
Corresponding Capacity | : |  | 100.0 | 100.0 | 62.5 | 55.7 | 59.2 | - | - | - | - | - | %
Total Cooling Capacity | : |  | 40.00 | 40.00 | 25.00 | 22.29 | 23.69 | - | - | - | - | - | TR
Total Cooling Capacity | : |  | 140.7 | 140.7 | 87.93 | 78.41 | 83.32 | - | - | - | - | - | kW
Total Power Input | : |  | 52.10 | 45.23 | 27.90 | 18.78 | 17.21 | - | - | - | - | - | kW
Total Current | : |  | 90 | 81 | 50 | 35 | 33 | - | - | - | - | - | A
COP | : |  | 2.700 | 3.110 | 3.152 | 4.175 | 4.841 | - | - | - | - | - | kW/kW
Ambient Temperature | : |  | 35.0 | 27.0 | 27.0 | 19.0 | 13.0 | - | - | - | - | - | °C
EEWT | : |  | 12.00 | 12.00 | 10.13 | 9.79 | 9.96 | - | - | - | - | - | °C
ELWT | : |  | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | - | - | - | - | - | °C
Flow Rate | : |  | 24.23 | 24.23 | 24.23 | 24.23 | 24.23 | - | - | - | - | - | m³/h
Pressure Drop | : |  | 51.2 | 51.2 | 51.2 | 51.2 | 51.2 | - | - | - | - | - | kPa
Others
MCA | : |  | 118 | [9 empty] | A
No. of Refrigerant Circuit | : |  | 1 | [9 empty] | -
Refrigerant Type : | : |  | R410A | [9 empty] | -
Refrigerant Charge : | : | System 1/2 | 25.0 / - | [9 empty] | kg/System
Chiller Dimension | : | W / D / H | 1146 / 3282 / 2156 | [9 empty] | mm
Weight | : | Shipping | 1130 | [9 empty] | kg
|  | Operating | 1139 | [9 empty] | kg
Evaporator
Type | : |  | BPHE | [9 empty] | -
Inlet/Outlet Diameter | : |  | 2.5" Male BSPT
Flow Rate | : | Min / Max | 10.00 / 32.50 | [9 empty] | m³/h
Pressure Drop | : | Min / Max | 5.80 / 94.7 | [9 empty] | kPa
Compressor
Quantity | : | System 1/2 | 2 / -
Type | : |  | Hermetic-sealed (Scroll) | [9 empty] | -
Oil Charge | : | System 1/2 | 13.4 / - | [9 empty] | L/System
Condenser
Coil
Tube | : | Type | Copper | [9 empty] | -
Fin | : | Type | Aluminium | [9 empty] | -
Surface Area/ Coil | : |  | 5.76 | [9 empty] | m²/Coil
Fan
Type/ Drive | : |  | Axial / Direct | [9 empty] | -
Quantity per System | : |  | 3 | [9 empty] | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 | [9 empty] | 15-Dec, 2022 08:31 |  |  | Page : 1/2