## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | :
Created By | :
Customer Input
Selected Model / Type | : | UAM60C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 25.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 11.00 | 60.56 | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 8.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 59.27 |  |  |  |  | 60.00 |  |  |  |  | TR
|  |  | 208.4 |  |  |  |  | 211.0 |  |  |  |  | kW
Current | : | Compressor | 115 |  |  |  |  | 99 |  |  |  |  | A
|  | Fan | 18 |  |  |  |  | 18 |  |  |  |  | A
|  | Total | 133 |  |  |  |  | 117 |  |  |  |  | A
Power Input | : | Compressor | 67.18 |  |  |  |  | 54.36 |  |  |  |  | kW
|  | Fan | 12.00 |  |  |  |  | 12.00 |  |  |  |  | kW
|  | Total | 79.18 |  |  |  |  | 66.36 |  |  |  |  | kW
COP | : |  | 2.632 |  |  |  |  | 3.180 |  |  |  |  | kW/kW
Flow Rate | : |  | 35.90 |  |  |  |  | 60.56 |  |  |  |  | m³/h
Pressure Drop | : |  | 37.9 |  |  |  |  | 88.9 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00°C, and ambient temperature of 35.0°C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m².K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.750 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Corresponding Capacity | : |  | 100.0 | 87.9 | 58.6 | 29.3 | - | - | - | - | - | - | %
Total Cooling Capacity | : |  | 60.00 | 52.76 | 35.17 | 17.59 | - | - | - | - | - | - | TR
Total Cooling Capacity | : |  | 211.0 | 185.6 | 123.7 | 61.85 | - | - | - | - | - | - | kW
Total Power Input | : |  | 66.36 | 50.77 | 33.18 | 17.59 | - | - | - | - | - | - | kW
Total Current | : |  | 117 | 89 | 59 | 31 | - | - | - | - | - | - | A
COP | : |  | 3.180 | 3.655 | 3.728 | 3.517 | - | - | - | - | - | - | kW/kW
Ambient Temperature | : |  | 25.0 | 25.0 | 25.0 | 25.0 | - | - | - | - | - | - | °C
EEWT | : |  | 11.00 | 10.64 | 9.76 | 8.88 | - | - | - | - | - | - | °C
ELWT | : |  | 8.00 | 8.00 | 8.00 | 8.00 | - | - | - | - | - | - | °C
Flow Rate | : |  | 60.56 | 60.56 | 60.56 | 60.56 | - | - | - | - | - | - | m³/h
Pressure Drop | : |  | 88.9 | 88.9 | 88.9 | 88.9 | - | - | - | - | - | - | kPa
Others
MCA | : |  | 3.750 1: 164 | A
No. of Refrigerant Circuit | : |  | 3.750 1: 2 | -
Refrigerant Type : | : |  | 3.750 1: R410A | -
Refrigerant Charge : | : | System 1/2 | 3.750 1: 21.0 / 21.0 | kg/System
Chiller Dimension | : | W / D / H | 3.750 1: 2237 / 3263 / 2156 | mm
Weight | : | Shipping | 3.750 1: 2052 | kg
|  | Operating | 3.750 1: 2174 | kg
Evaporator
Type | : |  | 3.750 1: S&T | -
Inlet/Outlet Diameter | : |  | 3.750 1: 4" Victaulic Joint
Flow Rate | : | Min / Max | 3.750 1: 13.70 / 61.20 | m³/h
Pressure Drop | : | Min / Max | 3.750 1: 7.00 / 90.0 | kPa
Compressor
Quantity | : | System 1/2 | 3.750 1: 2 / 2
Type | : |  | 3.750 1: Hermetic-sealed (Scroll) | -
Oil Charge | : | System 1/2 | 3.750 1: 13.4 / 13.4 | L/System
Condenser
Coil
Tube | : | Type | 3.750 1: Copper | -
Fin | : | Type | 3.750 1: Aluminium | -
Surface Area/ Coil | : |  | 3.750 1: 11.52 | m²/Coil
Fan
Type/ Drive | : |  | 3.750 1: Axial / Direct | -
Quantity per System | : |  | 3.750 1: 3 | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 |  |  | 3.750 8: 04-Jan, 2023 14:45 | Page : 1/2