## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | PRoject1
Created By | : | pendy
Customer Input
Selected Model / Type | : | UAMH68A3F |  |  | / | Inverter Speed (Hybrid) Scroll Chiller Version A
Ambient Temperature | : |  | 25.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | Flow Rate | 50.00 | 50.00 | m³/h |  |  | Voltage |  | : | 400 |  | V
|  | LWT | 8.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (MS Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 69.70 |  |  |  |  | 70.00 |  |  |  |  | TR
|  |  | 245.1 |  |  |  |  | 246.2 |  |  |  |  | kW
Current | : | Compressor | 124 |  |  |  |  | 84 |  |  |  |  | A
|  | Fan | 9 |  |  |  |  | 9 |  |  |  |  | A
|  | Total | 133 |  |  |  |  | 93 |  |  |  |  | A
Power Input | : | Compressor | 74.64 |  |  |  |  | 45.63 |  |  |  |  | kW
|  | Fan | 5.400 |  |  |  |  | 5.400 |  |  |  |  | kW
|  | Total | 80.04 |  |  |  |  | 51.03 |  |  |  |  | kW
COP | : |  | 3.063 |  |  |  |  | 4.824 |  |  |  |  | kW/kW
Flow Rate | : |  | 38.03 |  |  |  |  | 50.00 |  |  |  |  | m³/h
Pressure Drop | : |  | 25.9 |  |  |  |  | 39.2 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the MS2449 standard condition of EWT/LWT of 12.22/6.67°C, and ambient temperature of 35.0°C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m².K/kW, and rating altitute at 0 m.
Part Load Performance
MPLV | : |  | 3.850 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Corresponding Capacity | : |  | 100.0 | 90.0 | 80.0 | 70.0 | 60.0 | 50.0 | 40.0 | 30.0 | 20.0 | 12.2 | %
Total Cooling Capacity | : |  | 70.00 | 63.00 | 56.00 | 49.00 | 42.00 | 35.00 | 28.00 | 21.00 | 14.00 | 8.573 | TR
Total Cooling Capacity | : |  | 246.2 | 221.6 | 197.0 | 172.3 | 147.7 | 123.1 | 98.48 | 73.86 | 49.24 | 30.15 | kW
Total Power Input | : |  | 51.03 | 46.92 | 41.28 | 36.49 | 30.89 | 25.50 | 20.94 | 15.84 | 10.69 | 7.263 | kW
Total Current | : |  | 93 | 83 | 75 | 67 | 54 | 47 | 39 | 27 | 20 | 14 | A
COP | : |  | 4.824 | 4.723 | 4.771 | 4.723 | 4.782 | 4.827 | 4.702 | 4.661 | 4.604 | 4.151 | kW/kW
Ambient Temperature | : |  | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | °C
EEWT | : |  | 12.24 | 11.82 | 11.39 | 10.97 | 10.54 | 10.12 | 9.70 | 9.27 | 8.85 | 8.52 | °C
ELWT | : |  | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | 8.00 | °C
Flow Rate | : |  | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | m³/h
Pressure Drop | : |  | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | kPa
Others
MCA | : |  | 3.850 1: 175 | A
No. of Refrigerant Circuit | : |  | 3.850 1: 2 | -
Refrigerant Type : | : |  | 3.850 1: R410A | -
Refrigerant Charge : | : | System 1/2 | 3.850 1: 25.0 / 25.0 | kg/System
Chiller Dimension | : | W / D / H | 3.850 1: 2237 / 3263 / 2156 | mm
Weight | : | Shipping | 3.850 1: 2052 | kg
|  | Operating | 3.850 1: 2174 | kg
Evaporator
Type | : |  | 3.850 1: S&T | -
Inlet/Outlet Diameter | : |  | 3.850 1: 4" Victaulic Joint
Flow Rate | : | Min / Max | 3.850 1: 15.00 / 56.70 | m³/h
Pressure Drop | : | Min / Max | 3.850 1: 5.00 / 47.0 | kPa
Compressor
Quantity | : | System 1/2 | 3.850 1: 2 / 2
Type | : |  | 3.850 1: Hermetic-sealed (Scroll) | -
Oil Charge | : | System 1/2 | 3.850 1: 13.4 / 13.4 | L/System
Condenser
Coil
Tube | : | Type | 3.850 1: Copper | -
Fin | : | Type | 3.850 1: Aluminium | -
Surface Area/ Coil | : |  | 3.850 1: 11.52 | m²/Coil
Fan
Type/ Drive | : |  | 3.850 1: Axial / Direct | -
Quantity per System | : |  | 3.850 1: 3 | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 |  |  | 3.850 8: 06-Jan, 2023 15:53 | Page : 1/2