## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | Unilab
Created By | : | Lim Mei Yee
Customer Input
Selected Model / Type | : | UAM40CUM |  |  | / | Fixed Speed Scroll Chiller Version B
Ambient Temperature | : |  | 35.0 |  | °C |  |  | Frequency |  | : | 60 |  | Hz
Chilled Water | : | EWT | 12.00 | 21.63 | °C |  |  | Voltage |  | : | 380 |  | V
|  | LWT | 7.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (MS Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 39.64 |  |  |  |  | 40.11 |  |  |  |  | TR
|  |  | 139.4 |  |  |  |  | 141.1 |  |  |  |  | kW
Current | : | Compressor | 84 |  |  |  |  | 84 |  |  |  |  | A
|  | Fan | 11 |  |  |  |  | 11 |  |  |  |  | A
|  | Total | 94 |  |  |  |  | 94 |  |  |  |  | A
Power Input | : | Compressor | 44.91 |  |  |  |  | 44.95 |  |  |  |  | kW
|  | Fan | 4.500 |  |  |  |  | 4.500 |  |  |  |  | kW
|  | Total | 49.41 |  |  |  |  | 49.45 |  |  |  |  | kW
COP | : |  | 2.822 |  |  |  |  | 2.852 |  |  |  |  | kW/kW
Flow Rate | : |  | 21.63 |  |  |  |  | 24.29 |  |  |  |  | m³/h
Pressure Drop | : |  | 40.1 |  |  |  |  | 51.5 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the MS2449 standard condition of EWT/LWT of 12.22/6.67°C, and ambient temperature of 35.0°C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m².K/kW, and rating altitute at 0 m.
Part Load Performance
MPLV | : |  | - | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 2 | 4 | - | - | - | - | - | -
Corresponding Capacity | : |  | 100.0 | 70.1 | 70.1 | 37.7 | - | - | - | - | - | - | %
Total Cooling Capacity | : |  | 39.64 | 27.77 | 27.77 | 14.94 | - | - | - | - | - | - | TR
Total Cooling Capacity | : |  | 139.4 | 97.66 | 97.66 | 52.55 | - | - | - | - | - | - | kW
Total Power Input | : |  | 49.41 | 32.59 | 31.09 | 14.13 | - | - | - | - | - | - | kW
Total Current | : |  | 94 | 64 | 61 | 29 | - | - | - | - | - | - | A
COP | : |  | 2.822 | 2.997 | 3.142 | 3.718 | - | - | - | - | - | - | kW/kW
Ambient Temperature | : |  | 35.0 | 31.5 | 31.5 | 25.6 | - | - | - | - | - | - | °C
EEWT | : |  | 12.22 | 10.56 | 10.56 | 8.76 | - | - | - | - | - | - | °C
ELWT | : |  | 6.67 | 6.67 | 6.67 | 6.67 | - | - | - | - | - | - | °C
Flow Rate | : |  | 21.63 | 21.63 | 21.63 | 21.63 | - | - | - | - | - | - | m³/h
Pressure Drop | : |  | 40.1 | 40.1 | 40.1 | 40.1 | - | - | - | - | - | - | kPa
Others
MCA | : |  | 117 | [9 empty] | A
No. of Refrigerant Circuit | : |  | 1 | [9 empty] | -
Refrigerant Type : | : |  | R410A | [9 empty] | -
Refrigerant Charge : | : | System 1/2 | 25.0 / - | [9 empty] | kg/System
Chiller Dimension | : | W / D / H | 1146 / 3282 / 2156 | [9 empty] | mm
Weight | : | Shipping | 1078 | [9 empty] | kg
|  | Operating | 1087 | [9 empty] | kg
Evaporator
Type | : |  | BPHE | [9 empty] | -
Inlet/Outlet Diameter | : |  | 2.5" Male BSPT
Flow Rate | : | Min / Max | 10.00 / 32.50 | [9 empty] | m³/h
Pressure Drop | : | Min / Max | 5.80 / 94.7 | [9 empty] | kPa
Compressor
Quantity | : | System 1/2 | 3 / -
Type | : |  | Hermetic-sealed (Scroll) | [9 empty] | -
Oil Charge | : | System 1/2 | 20.1 / - | [9 empty] | L/System
Condenser
Coil
Tube | : | Type | Copper Tube | [9 empty] | -
Fin | : | Type | Aluminium Fin | [9 empty] | -
Surface Area/ Coil | : |  | 5.76 | [9 empty] | m²/Coil
Fan
Type/ Drive | : |  | Axial / Direct | [9 empty] | -
Quantity per System | : |  | 3 | [9 empty] | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 | [9 empty] | 17-May, 2023 16:41 |  |  | Page : 1/2