## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | Lee Ming Yang
Created By | : | DRMSA Software
Customer Input
Selected Model / Type | : | UAM100CFM |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 35.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 12.00 | 62.41 | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 7.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 103.0 |  |  |  |  | 103.0 |  |  |  |  | TR
|  |  | 362.4 |  |  |  |  | 362.4 |  |  |  |  | kW
Current | : | Compressor | 202 |  |  |  |  | 202 |  |  |  |  | A
|  | Fan | 24 |  |  |  |  | 24 |  |  |  |  | A
|  | Total | 226 |  |  |  |  | 226 |  |  |  |  | A
Power Input | : | Compressor | 115.8 |  |  |  |  | 115.8 |  |  |  |  | kW
|  | Fan | 16.00 |  |  |  |  | 16.00 |  |  |  |  | kW
|  | Total | 131.8 |  |  |  |  | 131.8 |  |  |  |  | kW
COP | : |  | 2.750 |  |  |  |  | 2.750 |  |  |  |  | kW/kW
Flow Rate | : |  | 62.41 |  |  |  |  | 62.41 |  |  |  |  | m³/h
Pressure Drop | : |  | 65.9 |  |  |  |  | 65.9 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00°C, and ambient temperature of 35.0°C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m².K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 4.035 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 2 | 3 | 3 | 4 | - | - | - | -
Corresponding Capacity | : |  | 100.0 | 80.2 | 63.4 | 53.1 | 34.9 | 28.1 | - | - | - | - | %
Total Cooling Capacity | : |  | 103.0 | 82.66 | 65.36 | 54.75 | 35.94 | 28.99 | - | - | - | - | TR
Total Cooling Capacity | : |  | 362.4 | 290.7 | 229.9 | 192.6 | 126.4 | 102.0 | - | - | - | - | kW
Total Power Input | : |  | 131.8 | 83.07 | 62.70 | 45.55 | 26.82 | 20.88 | - | - | - | - | kW
Total Current | : |  | 226 | 148 | 111 | 85 | 50 | 41 | - | - | - | - | A
COP | : |  | 2.750 | 3.500 | 3.666 | 4.228 | 4.713 | 4.883 | - | - | - | - | kW/kW
Ambient Temperature | : |  | 35.0 | 27.0 | 27.0 | 19.0 | 19.0 | 13.0 | - | - | - | - | °C
EEWT | : |  | 12.00 | 11.01 | 10.17 | 9.66 | 8.74 | 8.41 | - | - | - | - | °C
ELWT | : |  | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | - | - | - | - | °C
Flow Rate | : |  | 62.41 | 62.41 | 62.41 | 62.41 | 62.41 | 62.41 | - | - | - | - | m³/h
Pressure Drop | : |  | 65.9 | 65.9 | 65.9 | 65.9 | 65.9 | 65.9 | - | - | - | - | kPa
Others
MCA | : |  | 282 | [9 empty] | A
No. of Refrigerant Circuit | : |  | 2 | [9 empty] | -
Refrigerant Type : | : |  | R410A | [9 empty] | -
Refrigerant Charge : | : | System 1/2 | 35.0 / 35.0 | [9 empty] | kg/System
Chiller Dimension | : | W / D / H | 2237 / 4163 / 2156 | [9 empty] | mm
Weight | : | Shipping | 3048 | [9 empty] | kg
|  | Operating | 3239 | [9 empty] | kg
Evaporator
Type | : |  | S&T | [9 empty] | -
Inlet/Outlet Diameter | : |  | 5" Victaulic Joint
Flow Rate | : | Min / Max | 16.40 / 70.40 | [9 empty] | m³/h
Pressure Drop | : | Min / Max | 7.00 / 79.0 | [9 empty] | kPa
Compressor
Quantity | : | System 1/2 | 2 / 2
Type | : |  | Hermetic-sealed (Scroll) | [9 empty] | -
Oil Charge | : | System 1/2 | 13.4 / 13.4 | [9 empty] | L/System
Condenser
Coil
Tube | : | Type | Copper Tube | [9 empty] | -
Fin | : | Type | Aluminium Fin | [9 empty] | -
Surface Area/ Coil | : |  | 15.36 | [9 empty] | m²/Coil
Fan
Type/ Drive | : |  | Axial / Direct | [9 empty] | -
Quantity per System | : |  | 4 | [9 empty] | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 | [9 empty] | 27-Sep, 2024 19:02 |  |  | Page : 1/2