## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | : | Lee Ming Yang
Created By | : | DRMSA Software
Customer Input
Selected Model / Type | : | UAM60CUM |  |  | / | Fixed Speed Scroll Chiller Version B
Ambient Temperature | : |  | 35.0 |  | °C |  |  | Frequency |  | : | 60 |  | Hz
Chilled Water | : | EWT | 12.00 | 37.50 | °C |  |  | Voltage |  | : | 380 |  | V
|  | LWT | 7.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 61.92 |  |  |  |  | 61.92 |  |  |  |  | TR
|  |  | 217.8 |  |  |  |  | 217.8 |  |  |  |  | kW
Current | : | Compressor | 132 |  |  |  |  | 132 |  |  |  |  | A
|  | Fan | 21 |  |  |  |  | 21 |  |  |  |  | A
|  | Total | 153 |  |  |  |  | 153 |  |  |  |  | A
Power Input | : | Compressor | 70.76 |  |  |  |  | 70.76 |  |  |  |  | kW
|  | Fan | 9.000 |  |  |  |  | 9.000 |  |  |  |  | kW
|  | Total | 79.76 |  |  |  |  | 79.76 |  |  |  |  | kW
COP | : |  | 2.730 |  |  |  |  | 2.730 |  |  |  |  | kW/kW
Flow Rate | : |  | 37.50 |  |  |  |  | 37.50 |  |  |  |  | m³/h
Pressure Drop | : |  | 40.7 |  |  |  |  | 40.7 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00°C, and ambient temperature of 35.0°C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m².K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.988 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 2 | 3 | 3 | 4 | - | - | - | -
Corresponding Capacity | : |  | 100.0 | 79.9 | 64.1 | 52.7 | 35.3 | 28.2 | - | - | - | - | %
Total Cooling Capacity | : |  | 61.92 | 49.49 | 39.69 | 32.66 | 21.84 | 17.43 | - | - | - | - | TR
Total Cooling Capacity | : |  | 217.8 | 174.1 | 139.6 | 114.9 | 76.80 | 61.31 | - | - | - | - | kW
Total Power Input | : |  | 79.76 | 50.14 | 40.32 | 27.36 | 17.46 | 12.08 | - | - | - | - | kW
Total Current | : |  | 153 | 103 | 78 | 63 | 36 | 30 | - | - | - | - | A
COP | : |  | 2.730 | 3.472 | 3.462 | 4.198 | 4.398 | 5.076 | - | - | - | - | kW/kW
Ambient Temperature | : |  | 35.0 | 27.0 | 27.0 | 19.0 | 19.0 | 13.0 | - | - | - | - | °C
EEWT | : |  | 12.00 | 11.00 | 10.21 | 9.64 | 8.76 | 8.41 | - | - | - | - | °C
ELWT | : |  | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | - | - | - | - | °C
Flow Rate | : |  | 37.50 | 37.50 | 37.50 | 37.50 | 37.50 | 37.50 | - | - | - | - | m³/h
Pressure Drop | : |  | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | 40.7 | - | - | - | - | kPa
Others
MCA | : |  | 187 | [9 empty] | A
No. of Refrigerant Circuit | : |  | 2 | [9 empty] | -
Refrigerant Type : | : |  | R410A | [9 empty] | -
Refrigerant Charge : | : | System 1/2 | 21.0 / 21.0 | [9 empty] | kg/System
Chiller Dimension | : | W / D / H | 2237 / 3263 / 2156 | [9 empty] | mm
Weight | : | Shipping | 2052 | [9 empty] | kg
|  | Operating | 2174 | [9 empty] | kg
Evaporator
Type | : |  | S&T | [9 empty] | -
Inlet/Outlet Diameter | : |  | 4" Victaulic Joint
Flow Rate | : | Min / Max | 13.70 / 61.20 | [9 empty] | m³/h
Pressure Drop | : | Min / Max | 7.00 / 90.0 | [9 empty] | kPa
Compressor
Quantity | : | System 1/2 | 2 / 2
Type | : |  | Hermetic-sealed (Scroll) | [9 empty] | -
Oil Charge | : | System 1/2 | 10.3 / 10.3 | [9 empty] | L/System
Condenser
Coil
Tube | : | Type | Copper Tube | [9 empty] | -
Fin | : | Type | Aluminium Fin | [9 empty] | -
Surface Area/ Coil | : |  | 11.52 | [9 empty] | m²/Coil
Fan
Type/ Drive | : |  | Axial / Direct | [9 empty] | -
Quantity per System | : |  | 3 | [9 empty] | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 | [9 empty] | 30-Sep, 2024 14:33 |  |  | Page : 1/2