## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | :
Created By | :
Customer Input
Selected Model / Type | : | UAM60C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 35.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 12.00 |  | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 7.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 59.27 |  |  |  |  | 59.27 |  |  |  |  | TR
|  |  | 208.4 |  |  |  |  | 208.4 |  |  |  |  | kW
Current | : | Compressor | 115 |  |  |  |  | 115 |  |  |  |  | A
|  | Fan | 18 |  |  |  |  | 18 |  |  |  |  | A
|  | Total | 133 |  |  |  |  | 133 |  |  |  |  | A
Power Input | : | Compressor | 67.18 |  |  |  |  | 67.18 |  |  |  |  | kW
|  | Fan | 12.00 |  |  |  |  | 12.00 |  |  |  |  | kW
|  | Total | 79.18 |  |  |  |  | 79.18 |  |  |  |  | kW
COP | : |  | 2.632 |  |  |  |  | 2.632 |  |  |  |  | kW/kW
Flow Rate | : |  | 35.90 |  |  |  |  | 35.90 |  |  |  |  | m³/h
Pressure Drop | : |  | 37.9 |  |  |  |  | 37.9 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00°C, and ambient temperature of 35.0°C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m².K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.750 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 2 | 3 | 3 | 4 | - | - | - | -
Corresponding Capacity | : |  | 100.0 | 83.9 | 55.9 | 61.3 | 30.7 | 32.5 | - | - | - | - | %
Total Cooling Capacity | : |  | 59.27 | 49.72 | 33.14 | 36.34 | 18.17 | 19.27 | - | - | - | - | TR
Total Cooling Capacity | : |  | 208.4 | 174.8 | 116.6 | 127.8 | 63.91 | 67.76 | - | - | - | - | kW
Total Power Input | : |  | 79.18 | 52.47 | 36.32 | 31.96 | 15.98 | 14.61 | - | - | - | - | kW
Total Current | : |  | 133 | 91 | 63 | 58 | 29 | 27 | - | - | - | - | A
COP | : |  | 2.632 | 3.332 | 3.210 | 4.000 | 4.000 | 4.639 | - | - | - | - | kW/kW
Ambient Temperature | : |  | 35.0 | 27.0 | 27.0 | 19.0 | 19.0 | 13.0 | - | - | - | - | °C
EEWT | : |  | 12.00 | 11.19 | 9.80 | 10.07 | 8.53 | 8.63 | - | - | - | - | °C
ELWT | : |  | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | - | - | - | - | °C
Flow Rate | : |  | 35.90 | 35.90 | 35.90 | 35.90 | 35.90 | 35.90 | - | - | - | - | m³/h
Pressure Drop | : |  | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | - | - | - | - | kPa
Others
MCA | : |  | 164 | [9 empty] | A
No. of Refrigerant Circuit | : |  | 2 | [9 empty] | -
Refrigerant Type : | : |  | R410A | [9 empty] | -
Refrigerant Charge : | : | System 1/2 | 21.0 / 21.0 | [9 empty] | kg/System
Chiller Dimension | : | W / D / H | 2237 / 3263 / 2156 | [9 empty] | mm
Weight | : | Shipping | 2052 | [9 empty] | kg
|  | Operating | 2174 | [9 empty] | kg
Evaporator
Type | : |  | S&T | [9 empty] | -
Inlet/Outlet Diameter | : |  | 4" Victaulic Joint
Flow Rate | : | Min / Max | 13.70 / 61.20 | [9 empty] | m³/h
Pressure Drop | : | Min / Max | 7.00 / 90.0 | [9 empty] | kPa
Compressor
Quantity | : | System 1/2 | 2 / 2
Type | : |  | Hermetic-sealed (Scroll) | [9 empty] | -
Oil Charge | : | System 1/2 | 13.4 / 13.4 | [9 empty] | L/System
Condenser
Coil
Tube | : | Type | Copper | [9 empty] | -
Fin | : | Type | Aluminium | [9 empty] | -
Surface Area/ Coil | : |  | 11.52 | [9 empty] | m²/Coil
Fan
Type/ Drive | : |  | Axial / Direct | [9 empty] | -
Quantity per System | : |  | 3 | [9 empty] | -
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 | [9 empty] | 23-Dec, 2022 15:43 |  |  | Page : 1/2