## main
CHILLER SELECTION REPORT
Daikin Refrigeration Malaysia Sdn. Bhd.
Project | :
Created By | :
Customer Input
Selected Model / Type | : | UAM80C3F |  |  | / | Fixed Speed Scroll Chiller Version C
Ambient Temperature | : |  | 30.0 |  | °C |  |  | Frequency |  | : | 50 |  | Hz
Chilled Water | : | EWT | 11.00 |  | °C |  |  | Voltage |  | : | 380-415 |  | V
|  | LWT | 8.00 |  | °C |  |  | Country of Origin : |  | : | Malaysia
Generated Outputs
Full Load Performance |  |  | Nominal Data (AHRI Standard) |  |  |  |  | Input Conditions
Cooling Capacity | : |  | 80.00 |  |  |  |  | 80.00 |  |  |  |  | TR
|  |  | 281.4 |  |  |  |  | 281.4 |  |  |  |  | kW
Current | : | Compressor | 161 |  |  |  |  | 150 |  |  |  |  | A
|  | Fan | 18 |  |  |  |  | 18 |  |  |  |  | A
|  | Total | 179 |  |  |  |  | 168 |  |  |  |  | A
Power Input | : | Compressor | 92.20 |  |  |  |  | 83.34 |  |  |  |  | kW
|  | Fan | 12.00 |  |  |  |  | 12.00 |  |  |  |  | kW
|  | Total | 104.2 |  |  |  |  | 95.34 |  |  |  |  | kW
COP | : |  | 2.700 |  |  |  |  | 2.951 |  |  |  |  | kW/kW
Flow Rate | : |  | 48.45 |  |  |  |  | 53.87 |  |  |  |  | m³/h
Pressure Drop | : |  | 37.4 |  |  |  |  | 43.8 |  |  |  |  | kPa
Note | : | 1. Nominal data is based on the AHRI (551/591) standard condition of EWT/LWT of 12.00/7.00°C, and ambient temperature of 35.0°C.
2. Input Condition data is based on customer's input condition of EWT/LWT , and ambient temperature.
3. Evaporator rating fouling factor = 0.018 m².K/kW, and rating altitute at 0 m.
Part Load Performance
IPLV | : |  | 3.926 | [9 empty] | kW/kW
Point | : |  | 1 | 2 | 2 | 3 | 3 | 4 | - | - | - | -
Corresponding Capacity | : |  | 100.0 | 82.0 | 62.5 | 55.7 | 34.2 | 29.6 | - | - | - | - | %
Total Cooling Capacity | : |  | 80.00 | 65.59 | 50.00 | 44.59 | 27.37 | 23.69 | - | - | - | - | TR
Total Cooling Capacity | : |  | 281.4 | 230.7 | 175.9 | 156.8 | 96.25 | 83.32 | - | - | - | - | kW
Total Power Input | : |  | 104.2 | 66.57 | 51.80 | 37.56 | 22.79 | 17.21 | - | - | - | - | kW
Total Current | : |  | 179 | 118 | 93 | 69 | 43 | 33 | - | - | - | - | A
COP | : |  | 2.700 | 3.465 | 3.395 | 4.175 | 4.223 | 4.841 | - | - | - | - | kW/kW
Ambient Temperature | : |  | 35.0 | 27.0 | 27.0 | 19.0 | 19.0 | 13.0 | - | - | - | - | °C
EEWT | : |  | 12.00 | 11.10 | 10.13 | 9.79 | 8.71 | 8.48 | - | - | - | - | °C
ELWT | : |  | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | 7.00 | - | - | - | - | °C
Flow Rate | : |  | 48.45 | 48.45 | 48.45 | 48.45 | 48.45 | 48.45 | - | - | - | - | m³/h
Pressure Drop | : |  | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | - | - | - | - | kPa
Others
MCA | : |  | 223 | [9 empty] | A
No. of Refrigerant Circuit | : |  | 2 | [9 empty] | -
Refrigerant Type : | : |  | R410A | [9 empty] | -
Refrigerant Charge : | : | System 1/2 | 25.0 / 25.0 | [9 empty] | kg/System
Chiller Dimension | : | W / D / H | 2237 / 3263 / 2156 | [9 empty] | mm
Weight | : | Shipping | 2917 | [9 empty] | kg
|  | Operating | 3039 | [9 empty] | kg
Evaporator
Type | : |  | S&T | [9 empty] | -
Inlet/Outlet Diameter | : |  | 5" Victaulic Joint
Flow Rate | : | Min / Max | 15.00 / 56.70 | [9 empty] | m³/h
Pressure Drop | : | Min / Max | 5.00 / 47.0 | [9 empty] | kPa
Compressor
Quantity | : | System 1/2 | 2 / 2
Type | : |  | Hermetic-sealed (Scroll) | [9 empty] | -
Oil Charge | : | System 1/2 | 13.4 / 13.4 | [9 empty] | L/System
Condenser
Coil
Tube | : | Type | Copper | [9 empty] | -
Fin | : | Type | Aluminium | [9 empty] | -
Surface Area/ Coil | : |  | 11.52 | [9 empty] | m²/Coil
Fan
Type/ Drive | : |  | Axial / Direct | [9 empty] | -
Quantity per System | : |  | 3 | [9 empty] | -
Certified in accordance with the AHRI Air-Cooled Water-Chilling Packages Certification Program, which is based on AHRI Standard 550/590 (I-P) and AHRI Standard 551/591 (SI). Certified Units may be found in the AHRI Directory at www.ahridirectory.org
Note : For any enquiry, please contact your authorized sales agent.
CSQS.C01.S01 | [9 empty] | 12-Oct, 2022 06:32 |  |  | Page : 1/2